## ZONE 1
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 1 | Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
26-1116 Issue 12
Sheet 1 of 10
Sheet updated 03/04/2025

## ZONE 2
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 2 | Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
26-1116 Issue 12
Sheet 2 of 10
Sheet updated 03/04/2025

## ZONE 3
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 3 | Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
26-1116 Issue 12
Sheet 3 of 10
Sheet updated 03/04/2025

## ZONE 4
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 4 | Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
26-1116 Issue 12
Sheet 4 of 10
Sheet updated 03/04/2025

## ZONE 5
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 5 | Conventional Detector |  | 0.075 | 0 | 0.075 | 0 | 8 | 0
| Conventional MCP |  | 0 | 0 | 0 | 0 | 8 | 0
| Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
| Max Conventional Devices per zone = | 20
| Twinflex End of Line (mA) = | 0.5
26-1116 Issue 12
Sheet 5 of 10
Sheet updated 03/04/2025

## ZONE 6
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 6 | Conventional Detector |  | 0.075 | 0 | 0.075 | 0 | 8 | 0
| Conventional MCP |  | 0 | 0 | 0 | 0 | 8 | 0
| Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
| Max Conventional Devices per zone = | 20
| Twinflex End of Line (mA) = | 0.5
26-1116 Issue 12
Sheet 6 of 10
Sheet updated 03/04/2025

## ZONE 7
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 7 | Conventional Detector |  | 0.075 | 0 | 0.075 | 0 | 8 | 0
| Conventional MCP |  | 0 | 0 | 0 | 0 | 8 | 0
| Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
| Max Conventional Devices per zone = | 20
| Twinflex End of Line (mA) = | 0.5
26-1116 Issue 12
Sheet 7 of 10
Sheet updated 03/04/2025

## ZONE 8
| Company Name / Site Details. | Enter the quantity of each device in the orange quantity column below.
Company Name / Site Details.
| Company Name / Site Details. | If any cells are highlighted in red, that means that there is a problem
| Company Name / Site Details. | (see the red error message at the bottom of the page)
|  |  | STANDBY CURRENT |  | ALARM CURRENT |  | LOADING UNITS
| Item | Enter Quantity of Devices | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA) | DLU | Tot DLU
Devices on Zone 8 | Conventional Detector |  | 0.075 | 0 | 0.075 | 0 | 8 | 0
| Conventional MCP |  | 0 | 0 | 0 | 0 | 8 | 0
| Twinflex ASD no sounder |  | 0.056 | 0 | 0.15 | 0 | 1 | 0
| Twinflex ASD sounder - Low |  | 0.056 | 0 | 2.5 | 0 | 6.5 | 0
| Twinflex ASD sounder - High |  | 0.056 | 0 | 8 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, no sound |  | 0.056 | 0 | 2.6 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - Low |  | 0.056 | 0 | 4.9 | 0 | 8 | 0
| Twinflex ASD with sounder strobe, sounder - High |  | 0.056 | 0 | 10.5 | 0 | 16 | 0
| Twinflex Multipoint no sounder |  | 0.114 | 0 | 1.5 | 0 | 1.5 | 0
| Twinflex Multipoint sounder - Low |  | 0.114 | 0 | 3.5 | 0 | 3.5 | 0
| Twinflex Multipoint sounder - High |  | 0.114 | 0 | 8.5 | 0 | 8 | 0
| Twinflex MCP no sounder |  | 0 | 0 | 0 | 0 | 16 | 0
| Twinflex MCP with sounder – No sound |  | 0.345 | 0 | 2.16 | 0 | 16 | 0
| Twinflex MCP with sounder – Low |  | 0.345 | 0 | 11.58 | 0 | 27 | 0
| Twinflex MCP with sounder – High |  | 0.345 | 0 | 12.858 | 0 | 29 | 0
| Twinflex Flashpoint - Off |  | 0.223 | 0 | 6.81 | 0 | 16 | 0
| Twinflex Flashpoint – Low |  | 0.223 | 0 | 15.794 | 0 | 18 | 0
| Twinflex Flashpoint - High |  | 0.223 | 0 | 24.027 | 0 | 33 | 0
| Twinflex Soundpoint – Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Soundpoint – High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hipoint - Low |  | 0.185 | 0 | 12.619 | 0 | 13 | 0
| Twinflex Hipoint - High |  | 0.185 | 0 | 14.5 | 0 | 14.5 | 0
| Twinflex Hatari |  | 0.092 | 0 | 10.056 | 0 | 36 | 0
| Twinflex Output Module - Incompatible with Pro Panel |  | 5.092 | 0 | 34.13 | 0 | 34.5 | 0
(powered from panel)
| Twinflex Output Module - Incompatible with Pro Panel |  | 0.914 | 0 | 2.449 | 0 | 2.5 | 0
(with separate PSU)
| Twinflex Input Module (Callpoint Version) |  | 0.834 | 0 | 16 | 0 | 16 | 0
| Twinflex Input Module (Detector Version) |  | 0.834 | 0 | 20 | 0 | 20 | 0
| Twinflex Input Output Module |  | 0.207 | 0 | 22.715 | 0 | 23 | 0
| Twinflex Sounder/VAD - No Sounder |  | 0.144 | 0 | 16 | 0 | 18 | 0
| Twinflex Sounder/VAD - Low |  | 0.144 | 0 | 18 | 0 | 20 | 0
| Twinflex Sounder/VAD - High |  | 0.144 | 0 | 26 | 0 | 28 | 0
| Twinflex Sounder - Low |  | 0.144 | 0 | 3 | 0 | 3 | 0
| Twinflex Sounder - High |  | 0.144 | 0 | 11 | 0 | 11 | 0
| Add: Twinflex End of Line |  | 0.5 | 0 | 0.5 | 0
| Total Devices | 0 | Total IS | 0 | Total IA | 0 | Total DLU | 0
| Maximum DLUs per zone = | 160 |  |  |  |  | MAX DLUs = | 160
| Maximum Devices per zone = | 32
| Max Conventional Devices per zone = | 20
| Twinflex End of Line (mA) = | 0.5
26-1116 Issue 12
Sheet 8 of 10
Sheet updated 03/04/2025

## BATT CALC
| Company Name / Site Details. |  | Complete quantities in the orange 2-Zone or 4-Zone or 8-Zone Section.
| Company Name / Site Details. |  | Enter requirements in hours in the yellow boxes for Standby and Alarm.
Company Name / Site Details.
| Company Name / Site Details. |  | If panel outputs are used, enter "1" in the appropriate quantity column.
The maximum current for panel outputs is already entered in the corresponding
blue IS (mA) and IA (mA) boxes but can be changed to a lower figure if a
smaller load is used and you know the corresponding current consumption.
| Current Drawn From Panel PSU |  | Enter the number of detectors and callpoints to allow for being activated when calculating panel alarm current.
If any cells are highlighted in red, that means that there is a problem
| Where: IS = Standby Current, IA = Alarm Current |  | (see the red error message at the bottom of the page)
|  |  |  | STANDBY CURRENT |  | ALARM CURRENT |  | Dev | DLUs
| Item |  | Quantity | IS (mA) | Tot IS (mA) | IA (mA) | Tot IA (mA)
2-Zone Panel | Twinflex 2 Zone Panel |  |  | 27.5 | 0 | 27.5 | 0
| Twinflex 2/4 Zone Aux 24V O/P IF USED |  |  | 250 | 0 | 250 | 0
(MAX 250mA depending on external load)
| Twinflex 2/4 Zone MON O/P 1 IF USED |  |  | 0 | 0 | 250 | 0
(MAX 250mA depending on external load)
| Twinflex 2/4 Zone MON O/P 2 IF USED |  |  | 0 | 0 | 250 | 0
(MAX 250mA depending on external load)
4-Zone Panel | Twinflex 4 Zone Panel |  |  | 41 | 0 | 41 | 0
| Twinflex Repeater Panel powered from Aux 24V O/P |  |  | 16 | 0 | 50 | 0
This will reduce the Aux 24V O/P current by 50mA
| Twinflex 4 Zone Aux 24V O/P IF USED |  |  | 250 |  | 250
(MAX 250mA depending on external load)
| Twinflex 4 Zone MON O/P 1 IF USED |  |  | 0 | 0 | 250 | 0
(MAX 250mA depending on external load)
| Twinflex 4 Zone MON O/P 2 IF USED |  |  | 0 | 0 | 250 | 0
(MAX 250mA depending on external load)
8-Zone Panel | Twinflex 8 Zone Panel |  |  | 56 | 0 | 56 | 0
| Twinflex Repeater Panel powered from Aux 24V O/P |  |  | 16 | 0 | 50 | 0
This will reduce the Aux 24V O/P current by 50mA
| Twinflex 8 Zone Aux 24V O/P IF USED |  |  | 250 |  | 250
(MAX 250mA depending on external load)
| Twinflex 8 Zone MON O/P 1 IF USED |  |  | 0 | 0 | 200 | 0
(MAX 200mA depending on external load)
| Twinflex 8 Zone MON O/P 2 IF USED |  |  | 0 | 0 | 200 | 0
(MAX 200mA depending on external load)
Devices | Zone 1 (Enter details in the Zone 1 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 2 (Enter details in the Zone 2 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 3 (Enter details in the Zone 3 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 4 (Enter details in the Zone 4 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 5 (Enter details in the Zone 5 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 6 (Enter details in the Zone 6 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 7 (Enter details in the Zone 7 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Zone 8 (Enter details in the Zone 8 tab) |  |  |  | 0 |  | 0 | 0 | 0
| Add: Number of detectors activated in whole system |  |  |  |  | 48.5 | 0
| Up to 2 per zone out of a total of: | 14
| Add: Number of callpoints activated in whole system |  |  |  |  | 27.1 | 0
| Up to any number per zone out of a total of: | 7
| Totals |  |  | IStot (mA) A | 0 | IAtot (mA) B | 0 | PSU Max | 2100
| Times (hrs) |  |  | Standby (hrs) C | 24 | Alarm (hrs) D 0.25 to 0.5 | 0.5
| Current required (mAh) |  |  | IS (mAh) E | 0 | IA (mAh) F | 0
| Add: LCD Backlight for 20 minutes during alarm (20mA / 3) |  |  | Backlight / 12 | 0 | Backlight / 3 | 0
| and 5 minutes during fault (20mA / 12) |  |  |  |  | IA (mAh) G | 0
| Total Current (mAh) |  |  |  |  | E + G = H | 0
| Total Current (Ah) |  |  |  |  | H / 1000 = I | 0
| Battery requirement (Ah) |  |  |  |  | I x 1.25 = J | 0
| Actual Battery Capacity (Ah) | [5 empty] | 3.2
This will be hidden
| Maximum DLUs per zone = | 160 | [5 empty] | IA (mAh) | Battery | 1/20 mAh
| Maximum Devices per zone = | 32 | [5 empty] | 0 | 3.2 | 160mA
| Max Conventional Devices per zone = | 20 | [5 empty] | 0 | 3.3 | 165mA
| Twinflex End of Line (mA) = | 0.5 | [5 empty] | 0 | 3.4 | 170mA
[8 empty] | 0 | 7 | 350mA
| 26-1116 Issue 12 | [6 empty] | 0 | 7.2 | 360mA
Sheet 9 of 10
Sheet updated 03/04/2025

## DEVICE RATINGS
Company Name / Site Details. |  |  |  |  | DO NOT CHANGE ANYTHING ON THIS SHEET
Company Name / Site Details.
Company Name / Site Details.
Company Name / Site Details.
PRODUCT DESCRIPTION |  |  | DLU RATING @ SOUNDER LEVEL |  |  | CURRENT DRAWN
Type | Product Code | Subtype Name | SP0 - Off | Low | High | Quiescent | SP0 - Off | Low | High | Activated
DET |  | Conventional Detector | 8 | - | - | 0.075 | 0.075 | - | - | 20
MCP |  | Conventional MCP | 8 | - | - | 0 | 0 | - | - | 20
ASD | 204-0003 | Twinflex ASD no sounder | 1 | - | - | 0.056 | 0.15 | - | - | 8
ASD | 204-0001 | Twinflex ASD with sounder | 1 | 6.5 | 8 | 0.056 | 0.15 | 2.5 | 8 | 15.5
ASD | 204-0012 | Twinflex ASD with sounder strobe | 8 | 8 | 16 | 0.056 | 2.6 | 4.9 | 10.5 | 18
MP | 202-0001 | Twinflex Multipoint | 1.5 | - | - | 0.114 | 1.5 | - | - | 48.5
MPS | 202-0003 | Twinflex Multipoint with Sounder | 1.5 | 3.5 | 8 | 0.114 | 1.5 | 3.5 | 8.5 | 48.5
MCP | 402-0002, 402-0003, 402-0006 and 402-0007 | Twinflex Manual Call Point | 16 | - | - | 0 | 0 | - | - | 16.23
MCPS | 402-0012 | Twinflex Manual Call Point with Sounder | 16 | 27 | 29 | 0.345 | 2.16 | 11.58 | 12.858 | 27.1
SOUNDER | 302-0022 and 302-0012 | Twinflex Flashpoint | 16 | 18 | 33 | 0.223 | 6.81 | 15.794 | 24.027 | -
| 313-0021 and 313-0022 | Twinflex Soundpoint | - | 13 | 14.5 | 0.185 | - | 12.619 | 14.5 | -
| 302-0004 | Twinflex Hipoint | - | 13 | 14.5 | 0.185 | - | 12.619 | 14.5 | -
| 302-0001 and 302-0002 | Twinflex Hatari | - | - | 36 | 0.092 | - | - | 10.056 | -
I/O | 802-0001 | Twinflex Output Module - Powered from Panel | 34.5 | - | - | 5.092 | 34.13 | - | - | -
| 802-0001 | Twinflex Output Module - with separate PSU | 2.5 | - | - | 0.914 | 2.449 | - | - | -
| 802-0003 | Twinflex Input Module (Callpoint Version) | 16 | - | - | 0.834 | 16 | - | - | -
| 802-0002 | Twinflex Input Module (Detector Version) | 20 | - | - | 0.834 | 20 | - | - | -
| 802-0006 | Twinflex Input Output Module | 23 | - | - | 0.207 | 22.715 | - | - | -
TF SOUNDER/VAD | F0296336 | Twinflex Sounder/VAD | 18 | 20 | 28 | 0.144 | 16 | 18 | 26 | -
TF SOUNDER | F0296337 | Twinflex Sounder | - | 3 | 11 | 0.144 | - | 3 | 11 | -
MAX DLUs = |  | 160
Max Twinflex Devices per zone = |  | 32
Max Conventional Devices per zone = |  | 20
Twinflex End of Line (mA) = |  | 0.5
26-1116 Issue 12
Sheet 10 of 10
Sheet updated 03/04/2025